## Slide 1: My work with the ECAL DCS software and a Non-invasive isolation damage system for the preshower detector
Jakub Wieczorek
02/12/2019

## Slide 2: Presentation plan
  A few words about ECAL DCS
    What is that
    My participation
  Isolation damages detection project
    Problem definition
    Solution proposal
    Constructed systems
    Outcome

## Slide 3: ECAL Detector Control System

## Slide 4: ECAL DCS
  Detector Control System
  ECAL DCS one of the nodes of CMS DCS
  SCADA systems which allows controling and operating the detector
  My participation:
  Panel development
  Integration test for interlocks with final report
  Parts of technical documentation

## Slide 5
One panel for each partition
36 barel partitions, 8 endcaps partitions
352 temperature sensors
8 temperature sensors
per partition
1 water leakage sensor per endcap

## Slide 6: Temperature sensors plot widget
  Shows readouts from temperature sensors in real time
  Plot can be checked and unchecked by user
  When sensor is disabled there is no plot available for that sensor

## Slide 7: Conditions monitoring widget
  Partition conditions in real time
  When one of the temperature sensors exceeds threshold, then alarm and suitable automatic actions for the partition is perfomed
  Cooling status
  Water leakage available only for endcap partitions

## Slide 8: Interlock status widget
  Interlocks for current partition
  Temperature sensor exceeds limit, then high voltage, low voltage and low voltage cut interlocks are set
  Cooling interlock for water leakage sensors in endcaps
  Interlocks can be set manually

## Slide 9: Interlock status widget
  Crucial values for every sensor
  Wire connection
  Current value
  Warning status if value two degrees lower than overheating limit
  Crossing overheating limit causes partition interlocks
  Crossing critical overheating causes general DSS interlock, which turns off the detector

## Slide 10: Integration test for interlocks
Test for every partition – 352 temp + 8 WLD
1) Set value to fake sensor – exceed threshold
2) Check if interlocks is set
3) Come back to the normal state and acknowledge interlocks
5) Check if DSS interlock set
4) Exceed critical threshold
6) Exceed WLD threshold
7) Check if COOL interlock set
  Problems with 2 sensors detected!

## Slide 11: Isolation damages detection project

## Slide 12: Introduction and problem definition
The CMS Preshower detector is cooled down to -20°C by C6F14 based liquid
Pipes are isolated using Armaflex
Armaflex is subjected to ageing and damage
Air gets inside an isolation and condensates on the pipes
Energy dissipation

## Slide 13: Solution proposal #1
Cut the isolation
Mount humidity and temperature sensors
Connect sensors to PLC
Build SCADA system
Detect isolation damages
Replace damaged isolation
What are the problems?

## Slide 14: Solution proposal #2
Use simple sensors, radiation resistant – pair of needles
Stick them into isolation and measure resistance
Measuring infinite resistance – isolation not broken
Measuring something else – potential isolation damage
What are the problems?

## Slide 15: Few words about measurements
It matters where needles are stuck
Really difficult to measure something between no water and water
Water typically several hundreds of kΩ
Dry isolation typically dozen MΩ

## Slide 16: Hardware and electronics
Pair of needles
  100% radiation resistant
  Potentially subject to rust
High valued resistor
Voltage divider

## Slide 17: Microcontroller
ARM Cortex M3
STM32F103RBT6 on the Nucleo board
  Price 10chf on Digi-Key
  Community
  Very fast microcontroller with many periphals – 2xADC 16 channels each
HAL Library, no CUBE MX code generation
C++
Few words about logic
  ADC readout using DMA every second
  Average of 20 readouts
  Transfer data by UART using DMA

## Slide 18: Raspberry OPC UA Server
Raspberry PI 4
Ubuntu Docker image
  docker-compose
  Very easy to configure and run server – one comand
OPC UA Server
  Generic industrial protocol
  Easy to transfer data to SCADA
  Python 3.7 implementation using opcua library
Why raspberry?
Impossible to deploy OPC Server on microcontroller

## Slide 19: SCADA
Front-end part of the system
Panel (widget) to visualize data
Alarms
WinCC OA 3.16 Patch 15, JCOP 8.4.0 Beta
Simple instalation of the component
  Adding managers
  Configuring addresses
  Establishing connection with OPC UA Server

## Slide 20: Project outcome

## Slide 21: Future work
Test system in real operational environment
Adapt to the new conditions – change resistors, change thresholds
Add more set of needles and measure over a whole length

## Slide 22
https://gitlab.cern.ch/jawieczo/isolationverifier
jakub.lukasz.wieczorek@cern.ch